## Slide 1
Delta VFD-M Series
Variable Frequency Drive (VFD)
Complete Industrial Training Course
Sensorless Vector Control Micro Drive | AC Motor Speed Control
Instructor: ________________________ Date: ___________
Delta Electronics | VFD Training Division

## Slide 2
Course Outline
Delta VFD-M Series — Complete Training Program
Module 01
Introduction to Variable Frequency Drives (VFD)
Module 02
Delta VFD-M Series — Overview & Specifications
Module 03
Safety Guidelines & Precautions
Module 04
Mechanical Installation & Mounting
Module 05
Electrical Wiring — Power & Control Terminals
Module 06
Digital Keypad Operation & Display
Module 07
Parameter Programming (P00 – P09 Groups)
Module 08
Control Modes & Speed Reference
Module 09
Motor Auto-Tuning & Performance Optimization
Module 10
Protective Functions & Fault Diagnosis
Module 11
Industrial Application Examples
Module 12
Maintenance, Troubleshooting & Best Practices

## Slide 3
Module 01 — Introduction to Variable Frequency Drives
What is a VFD? Why do we use it?
What is a VFD?
▶ A VFD (Variable Frequency Drive) is an electronic device that controls the speed of an AC induction motor
▶ It varies the frequency & voltage supplied to the motor
▶ Also known as: Inverter, AC Drive, Frequency Converter
▶ Works on V/F (Volts per Hertz) or Sensorless Vector principle
▶ Input: Fixed AC supply (50/60 Hz)
▶ Output: Variable frequency & variable voltage to motor
Why Use a VFD?
▶ Precise motor speed control (0 – max RPM)
▶ Soft start / soft stop → reduces mechanical stress
▶ Energy saving: up to 50% electricity savings on fans & pumps
▶ Reduces inrush current at startup
▶ Overload & short-circuit protection
▶ Forward / Reverse control
▶ Multiple speed presets
▶ Smooth acceleration & deceleration ramps

## Slide 4
Module 01 — VFD Working Principle & Types
How AC drives work internally
VFD Internal Power Flow
AC Mains → Rectifier (AC→DC) → DC Bus (Capacitor Bank) → IGBT Inverter (DC→Variable AC) → Motor PWM (Pulse Width Modulation) used to synthesise variable frequency output Carrier frequency: typically 2 kHz – 15 kHz (P03.00 in VFD-M)
Control Methods
V/F Control: Maintains constant V/Hz ratio — simple, good for fans/pumps Sensorless Vector Control (SVC): Estimates rotor flux without encoder — high torque at low speed Delta VFD-M uses SVC as default — superior low-speed torque
Common VFD Applications
Pumps & Water Treatment Plants HVAC Fans & Air Compressors Conveyor Belts & Material Handling CNC Routers, Lathes & Milling Machines Treadmills & Fitness Equipment Textile & Packaging Machines
Key Terminology
Frequency (Hz) ↔ Motor Speed (RPM): N = (120 × f) / P Base Frequency: rated frequency of motor (50 Hz) Max Output Frequency: can exceed base (field weakening zone) Acceleration Time: time to ramp from 0 → max speed Deceleration Time: time to ramp from max speed → 0

## Slide 5
Module 02 — Delta VFD-M Series Overview
Product family, model code, and key specifications
Product Introduction
Manufacturer: Delta Electronics, Inc. (Taiwan) Series: VFD-M — General Purpose Sensorless Vector Micro Drive Technology: Latest microprocessor + IGBT switching Standard: CE, UL, cUL certified
Model Code Breakdown e.g. VFD007M21A
VFD = Variable Frequency Drive product family 007 = 0.75 kW (007 = 0.75kW, 015=1.5kW, 022=2.2kW, 037=3.7kW…) M = M Series 2 = Voltage class: 1=115V, 2=230V, 4=460V 1 = Phase: 1=Single phase, 3=Three phase A = Version / Enclosure
Power & Voltage Ratings
115V Series: 0.2 kW – 0.75 kW (0.25 – 1 HP) 230V 1-Phase: 0.4 kW – 2.2 kW (0.5 – 3 HP) 230V 3-Phase: 0.4 kW – 5.5 kW (0.5 – 7.5 HP) 460V 3-Phase: 0.75 kW – 5.5 kW (1 – 7.5 HP) 575V 3-Phase: 0.75 kW – 7.5 kW (1 – 10 HP)
Electrical Specifications
Output Frequency: 0.1 – 400 Hz Carrier Frequency: 1 – 15 kHz (adjustable) Frequency Accuracy: ±0.01 Hz (digital ref) Overload Capacity: 150% rated current for 60 s Protection: IP20 / NEMA 1 Operating Temp: -10°C to +40°C (non-condensing)
Key Features at a Glance
Sensorless vector control for high torque at low speed | Built-in PID controller RS-485 Modbus RTU communication | Analog input: 0–10V / 4–20mA Multi-speed presets (up to 15 speeds) | Skip frequency bands DC braking | Dynamic braking resistor support | Auto-restart after fault

## Slide 6
Module 02 — External Components & Accessories
Parts of the VFD-M unit and optional accessories
External Parts of VFD-M Unit
▶ Digital Keypad (KPV-CE01) — display & programming
▶ Power Terminal Block: R, S, T (Input); U, V, W (Output); B1, B2 (Braking)
▶ Control Terminal Block: Analog & Digital I/O
▶ Grounding Terminal (PE)
▶ Cooling Fan (on larger models)
▶ DIN Rail / Panel Mount Bracket
▶ RS-485 Communication Port (RJ-45)
▶ Charge Indicator LED
Optional Accessories
▶ Remote Keypad Extension Cable
▶ Dynamic Braking Resistor (for fast decel)
▶ EMI / RFI Filter (for CE compliance)
▶ AC Line Reactor (input harmonic reduction)
▶ DC Bus Reactor
▶ Zero-Phase Reactor
▶ RS-485 to USB Converter for PC programming
▶ Delta WPLSoft / DIADesigner Software

## Slide 7
Module 03 — Safety Guidelines & Precautions
DANGER / WARNING / CAUTION — Read before installation
⚠ DANGER
• ALWAYS disconnect AC mains before wiring • Wait 10 minutes after power-off for capacitors to discharge • Never open the drive while power is ON • High voltage present on R/S/T and U/V/W terminals
⚠ WARNING
• Do NOT connect AC power to U/V/W motor terminals • Ground the drive properly (PE terminal) • Never touch internal components or PCB • Motor cable must be shielded for EMI reduction
ℹ CAUTION
• Only qualified personnel should install, wire, and program the drive • Do not install near heat sources or in high-humidity environments • Ensure adequate ventilation — minimum clearance 10 cm on all sides • Use copper conductors only; tighten all terminals to specified torque
PPE & Tools Required
Personal Protective Equipment: Insulated gloves, safety glasses, voltage tester Tools: Insulated screwdrivers, torque wrench, multimeter, clamp meter Lockout/Tagout (LOTO) procedure must be followed before any maintenance work

## Slide 8
Module 04 — Mechanical Installation & Mounting
Site selection, mounting clearances, and environmental conditions
Site & Environmental Requirements
▶ Ambient Temperature: -10°C to +40°C (derate above 40°C)
▶ Humidity: 90% RH max — non-condensing
▶ Altitude: ≤1000 m (derate above 1000 m)
▶ Vibration: ≤0.6G (20–50 Hz); ≤1G (< 20 Hz)
▶ Storage Temp: -20°C to +60°C
▶ Keep away from: direct sunlight, rain, dust, corrosive gas
▶ Atmospheric Pressure: 86 – 106 kPa
▶ Install in IP54 enclosure for dusty environments
Mounting Procedure
▶ Mount VERTICALLY on panel or DIN rail
▶ Minimum clearances: 10 cm top & bottom, 5 cm left & right
▶ Do NOT mount horizontally or upside-down
▶ Use M4 or M5 screws with proper torque
▶ Multiple VFDs: stagger or provide side vents
▶ Ensure cooling air flows bottom to top
▶ Remove the protective film before powering on
▶ Check nameplate voltage matches supply before wiring

## Slide 9
Module 05 — Power Terminal Wiring
R/S/T input, U/V/W output, braking and grounding
Power Input Terminals (R, S, T)
R, S, T → 3-phase AC mains input (or R, T for single-phase models) Always connect through MCCB (Moulded Case Circuit Breaker) or fuse Never connect motor cable to R/S/T — this will DESTROY the drive Recommended: add AC line reactor at input for harmonic reduction
Power Output Terminals (U, V, W)
U, V, W → Connect to motor terminals (3-phase) Do NOT install contactors between drive output and motor If contactors are needed, interlock with VFD run signal Use shielded cable; connect shield to PE at both ends
Braking & DC Bus Terminals
B1, B2 → External braking resistor connection Braking resistor needed for applications with high inertia loads +1, +2 → DC bus terminals for DC bus reactor (harmonic filter) Never short-circuit the DC bus terminals
Grounding (PE) & Cable Sizing
Always connect PE (protective earth) to chassis ground Separate ground conductor required — do NOT share neutral Cable sizing: follow NEC/IEC based on drive rated current Tighten terminals to specified torque (see manual table)
Wiring Sequence (Safe Practice)
Step 1: Install MCCB/fuse → Step 2: Wire R/S/T input → Step 3: Wire U/V/W to motor → Step 4: Connect PE ground → Step 5: Wire control terminals → Step 6: Verify all connections before power-on

## Slide 10
Module 05 — Control Terminal Wiring
Digital inputs, analog inputs, relay outputs, and RS-485
Digital Input Terminals
▶ FWD (MI1) — Forward Run command
▶ REV (MI2) — Reverse Run command
▶ MI3 – MI6 — Multi-function inputs (programmable)
  • Common functions: Multi-speed, Jog, External fault, Reset
▶ DCM — Digital common (0V reference)
▶ COM — Common for digital outputs
▶ Logic: NPN (sink) or PNP (source) selectable via jumper
▶ Input voltage: 24VDC internal or external supply
Analog & Output Terminals
▶ AVI — Analog Voltage Input: 0–10V (speed reference)
▶ ACI — Analog Current Input: 4–20 mA (speed reference)
▶ ACM — Analog Common
▶ AFM — Analog Frequency/Current Output (0–10V or 0–20mA)
▶ MO — Multi-function Open Collector Output
▶ RA, RB, RC — Relay output (250VAC / 30VDC, 1A)
▶ RS-485 port: Modbus RTU, 9600–115200 baud
▶ +10V, GND — for external potentiometer (speed pot)

## Slide 11
Module 06 — Digital Keypad Operation (KPV-CE01)
Keypad layout, LED display, navigation and status indicators
Keypad Buttons & Functions
▶ ▶ RUN — Start the motor (when keypad control mode)
▶ ⏹ STOP — Stop the motor / Reset fault
▶ ▲ UP — Increase frequency / Scroll parameter up
▶ ▼ DOWN — Decrease frequency / Scroll parameter down
▶ FWD/REV — Toggle forward/reverse direction
▶ PROG/DATA — Enter parameter programming mode
▶ ENTER — Confirm parameter value / Enter sub-menu
▶ RESET — Reset fault condition
LED Display & Indicators
▶ 5-digit 7-segment LED display
▶ Shows: Output frequency (Hz), Output voltage (V),
  • Output current (A), DC bus voltage, RPM
▶ RUN LED — ON when drive is running
▶ FWD LED — ON for forward direction
▶ REV LED — ON for reverse direction
▶ FAULT LED — ON when fault present
▶ Hz / A / V indicator LEDs for unit display

## Slide 12
Module 07 — Parameter Groups Overview (P00 – P09)
Complete parameter group structure of VFD-M Series
P00
Drive Parameters
Max/Min frequency, base freq, control mode, speed ref source
P01
Basic Parameters
Acceleration/Deceleration time (1&2), Jog freq, Jog accel/decel
P02
Operation Method
Run/Stop source, direction lock, momentary power loss restart
P03
Output Function
Carrier frequency, slip compensation, AVR control, over-voltage stall
P04
Input Function
Multi-function input terminal (MI3–MI6) configuration
P05
Output Function
Multi-function output (MO, relay RA/RB) configuration
P06
Protection
OL1 (motor overload), OC (over-current), OV (over-voltage) settings
P07
Motor Parameters
Motor rated voltage, current, frequency, poles, no-load current
P08
Special Parameters
DC braking, speed search, PID control enable
P09
Communication
RS-485 address, baud rate, parity, Modbus protocol settings

## Slide 13
Module 07 — Key Parameters: P00 & P01 (Drive & Basic)
Frequency settings, acceleration/deceleration time programming
Param
Name
Default
Range
Description
P00.00
Max Output Frequency
50.00 Hz
0.10–400.0 Hz
Sets the maximum output frequency
P00.01
Motor Base Frequency
50.00 Hz
0.10–400.0 Hz
Motor rated frequency (nameplate)
P00.02
Motor Rated Voltage
220V / 380V
Depends on model
Motor nameplate voltage
P00.03
Output Freq Limit High
50.00 Hz
0 – P00.00
Upper frequency clamp
P00.04
Output Freq Limit Low
0.00 Hz
0 – P00.03
Lower frequency clamp (min speed)
P00.05
Control Mode
0
0=V/F, 2=SVC
Select V/F or Sensorless Vector
P00.06
Frequency Command Source
0
0=Keypad, 1=AVI, 2=ACI, 3=RS485
Speed reference source
P00.07
Run/Stop Command Source
0
0=Keypad, 1=External terminal
Control source selection

## Slide 14
Module 07 — Important Parameters: P01, P02, P07
Accel/Decel, Run source, Motor auto-tune parameters
P01 — Basic Parameters (Accel/Decel)
P01.00 Accel Time 1: Default 10s | Range: 0.1–600s — Time to ramp from 0 to max freq P01.01 Decel Time 1: Default 10s | Range: 0.1–600s — Time to ramp from max to 0 P01.02 Accel Time 2: Secondary accel time (switched via MI terminal) P01.03 Decel Time 2: Secondary decel time P01.04 Jog Frequency: Default 6 Hz | Used when JOG command activated P01.05 Jog Accel/Decel: Separate accel/decel time for jog operation
P02 — Operation Method
P02.00 Run/Stop Source: 0=Keypad, 1=Terminal, 2=RS-485 P02.01 Frequency Source: 0=Keypad UP/DN, 1=AVI (0–10V), 2=ACI (4–20mA), 3=RS-485 P02.02 Momentary Power Loss Restart: 0=Disable, 1=Enable (drive restarts after power recovery) P02.03 Direction Lock: 0=Both, 1=FWD only, 2=REV only
P07 — Motor Parameters (for Auto-Tune)
P07.00 Motor Rated Voltage (V) — enter motor nameplate value P07.01 Motor Rated Current (A) — enter motor nameplate FLA P07.02 Motor Base Frequency (Hz)— usually 50 Hz P07.03 Motor Rated RPM — e.g. 1450 RPM for 4-pole 50 Hz motor P07.04 Number of Motor Poles — e.g. 4 P07.05 No-load Current (A) — measured during auto-tune; improves SVC accuracy

## Slide 15
Module 08 — Control Modes & Speed Reference Methods
Keypad, analog input, multi-speed, RS-485, and PID control
Speed Reference Sources
▶ Keypad Control (P00.06=0): Use ▲/▼ keys to set frequency
▶ Analog Voltage AVI (P00.06=1): 0–10V potentiometer
  • 0V = 0 Hz, 10V = Max Frequency
▶ Analog Current ACI (P00.06=2): 4–20 mA signal
  • 4mA = 0 Hz, 20mA = Max Frequency
▶ RS-485 Modbus (P00.06=3): PC or PLC sets frequency via protocol
▶ Multi-Speed Presets (P04 group): Up to 15 fixed speeds
▶ PID Output: Process feedback control (e.g., pressure, flow)
Run / Stop Command Sources
▶ Keypad (P02.00=0): RUN / STOP keys on keypad
▶ External Terminal (P02.00=1):
  • FWD terminal → motor runs forward
  • REV terminal → motor runs reverse
  • Both open → motor stops
▶ RS-485 (P02.00=2): Remote Modbus command
▶ Jog Mode: Momentary run at jog frequency (P01.04)
▶ Multi-Function Inputs (MI3–MI6): map to speed, fault reset, etc.

## Slide 16
Module 09 — Motor Auto-Tuning & Performance Optimization
V/F curve, slip compensation, and sensorless vector tuning
Auto-Tuning Procedure (Step-by-Step)
1. Enter motor nameplate data into P07.00–P07.04 2. Set P05.00 = 12 (Auto-Tuning function) on a Multi-Function output or via keypad 3. Press RUN → Drive will energize motor and measure: stator resistance, leakage inductance 4. Results stored automatically in P07.05 (no-load current) and related registers 5. After tune complete: verify performance by running motor at low speed (5–10 Hz)
V/F Curve Settings (P00 group)
Linear V/F: Constant torque loads (conveyors, compressors) — voltage increases linearly with freq Square V/F: Variable torque (fans, pumps) — energy efficient, voltage increases as square of freq Custom V/F: P03.00–P03.03 define up to 4 V/F breakpoints for special motor requirements Base Frequency (P00.01): Match to motor nameplate (50 Hz in Bangladesh/India)
Slip Compensation & DC Braking
Slip Compensation (P03.07): Compensates for speed drop under load Higher value → better speed regulation under varying loads DC Braking (P08.00–P08.03): P08.00 = DC braking current (%) P08.01 = DC braking time at start P08.02 = DC braking time at stop Use for: hoists, cranes, precise stop applications
Performance Tips
Increase carrier frequency (P03.00) for quieter motor operation (reduces audible noise) Enable AVR (P03.08=1): Auto-Voltage Regulation maintains stable output during input fluctuation Stall prevention (P06.01): Prevents drive trip during acceleration with heavy loads Skip frequencies (P04.13–P04.15): Avoid mechanical resonance frequencies

## Slide 17
Module 10 — Protective Functions & Fault Codes (Part 1)
Over-current, over-voltage, under-voltage, overload faults
Code
Fault
Cause
Corrective Action
OC
Over-Current
Output current exceeded trip level (150–200% rated)
Reduce load, increase accel time, check motor wiring
OV
Over-Voltage
DC bus voltage too high (> ~410V for 230V model)
Add braking resistor, increase decel time
UV
Under-Voltage
DC bus too low — mains supply dropout
Check power supply, check MCCB, check input fuses
OL1
Motor Overload
Motor overloaded based on I²t calculation
Reduce load, check motor size, set P06.01 correctly
OL2
Drive Overload
Drive itself overloaded — 150% for >60s
Reduce load, upgrade to higher rated drive
OH
Overheat
Heat sink temperature too high (>85°C)
Clean cooling fins, check ambient temp, improve ventilation
PHL
Phase Loss
One or more input or output phases missing
Check R/S/T connections, check fuses, check motor cable
GFF
Ground Fault
Ground leakage current detected
Check motor insulation, check cable shields

## Slide 18
Module 10 — Fault Codes (Part 2) & Protection Settings
Communication faults, hardware faults, and protection parameters
Code
Fault
Cause
Corrective Action
EF
External Fault
Fault signal received on MI terminal (EF function assigned)
Check external device/sensor, clear fault, reset
CF1
Memory Read Error
EEPROM internal error
Press RESET; if persists replace keypad/PCB
CF3
CPU Error
Internal processor fault
Power cycle drive; contact Delta service
LV
Low Voltage Warning
Input voltage dropped below threshold
Check mains voltage; enable auto-restart if needed
CE1
Comm Frame Error
RS-485 data frame error
Check baud rate (P09.01), parity (P09.02) settings
CE2
Comm Checksum Error
Modbus CRC/LRC mismatch
Check cable shielding, cable length < 500m
SE
Speed Error (SVC)
Motor speed feedback error in SVC mode
Re-run auto-tune, check motor parameters
Fault Reset Methods
Method 1: Press STOP/RESET key on keypad Method 2: Toggle EF reset terminal (MI assigned to Reset) Method 3: Send Modbus reset command via RS-485 Method 4: Power cycle (OFF → wait 5s → ON) — only if fault is cleared

## Slide 19
Module 11 — Industrial Application: Pump & Fan Control
Constant pressure water supply using PID control
Application: Constant Pressure Water Pump System
Sensor: Pressure transducer → 4–20 mA signal to ACI terminal Setpoint: Desired pressure entered as P08.10 (PID setpoint) PID Action: Drive varies motor speed to maintain constant pressure Benefits: Energy saving, eliminates pressure surges, extends pump life
PID Parameter Settings
P08.10 — PID Setpoint (target value, 0–100%) P08.11 — PID Feedback Source: 1=ACI (4–20mA pressure transducer) P08.12 — Proportional Gain (Kp): Higher = faster response P08.13 — Integral Time (Ti): Lower = more aggressive integration P08.14 — Derivative Time (Td): Reduces overshoot P08.15 — PID Output Upper Limit / Lower Limit
Fan Speed Control (Energy Saving)
Use Square V/F curve (P03.06 = 2) for centrifugal fans/pumps Speed reduction from 100% to 80% → power drops to ~51% Speed reduction from 100% to 50% → power drops to ~12.5% P(speed) ∝ Speed³ — Affinity Law for centrifugal loads ROI on VFD installation: typically < 18 months
Typical Parameter Setup: 5.5 kW Water Pump
P00.01=50Hz, P00.03=50Hz, P00.04=20Hz | P01.00=15s, P01.01=15s | P02.00=1 (terminal), P02.01=2 (ACI 4-20mA) | P07.01=11A (motor FLA) | P08.10=60% (setpoint), P08.11=1 (ACI feedback)

## Slide 20
Module 11 — Application: CNC / Conveyor / Multi-Speed
Spindle control, conveyor preset speeds, and RS-485 Modbus
CNC Router Spindle Control
▶ Use AVI (0–10V) from CNC controller to AVI terminal
▶ P00.06 = 1 (AVI frequency source)
▶ P00.02 = 1 (External terminal run/stop)
▶ P00.00 = 400 Hz (max for spindle motor)
▶ P01.00 = 3s, P01.01 = 3s (fast accel/decel)
▶ P03.00 = 12 kHz (high carrier for quiet operation)
▶ P07.01 = spindle motor FLA
▶ Auto-tune P07 parameters for best performance
Conveyor Multi-Speed Preset
▶ Up to 15 speed presets via MI terminals
▶ MI3 + MI4 combination selects speed 1–15
▶ P04.05 = Speed 1 (e.g. 10 Hz — slow)
▶ P04.06 = Speed 2 (e.g. 25 Hz — medium)
▶ P04.07 = Speed 3 (e.g. 40 Hz — fast)
▶ P04.08 = Speed 4 (e.g. 50 Hz — full speed)
▶ PLC controls MI terminals for automatic speed selection
▶ Relay output configured to signal 'at speed' status

## Slide 21
Module 12 — Preventive Maintenance Schedule
Daily, monthly, semi-annual, and annual checks
Daily Checks
✔ Check for unusual noise or vibration from motor ✔ Monitor output frequency and current on display ✔ Verify cooling fan is running (larger models) ✔ Check ambient temperature is within spec
Monthly Checks
✔ Clean air vents and heat sink fins (compressed air) ✔ Check all terminal screws for looseness ✔ Inspect power cables for insulation damage ✔ Verify control terminal connections are secure
Semi-Annual Checks
✔ Measure input voltage balance (all 3 phases) ✔ Check motor insulation with megger (>1 MΩ) ✔ Inspect capacitors for bulging or leakage ✔ Test relay output contacts for wear
Annual Checks
✔ Replace cooling fan if noisy or slow (lifespan ~3 years) ✔ Check electrolytic capacitors (lifespan 5–10 years) ✔ Full parameter backup via keypad or RS-485 ✔ Load test drive at full capacity; log current readings

## Slide 22
Module 12 — Troubleshooting Guide & Best Practices
Common problems, solutions, and pro tips
Common Troubleshooting Scenarios
▶ Problem: Motor doesn't start
  • → Check run source (P02.00), check FWD/REV terminal
  • → Check min frequency P00.04 is not too high
▶ Problem: Motor runs but wrong speed
  • → Check P00.06 (freq source), verify AVI/ACI signal
▶ Problem: OC fault on start
  • → Increase accel time P01.00
  • → Check for locked rotor / mechanical jam
▶ Problem: OV fault on stop
  • → Increase decel time P01.01
  • → Install braking resistor (B1-B2 terminals)
Best Practices & Pro Tips
▶ Always back up parameters before changes (note down all Pxx values)
▶ Use shielded cable for motor wiring > 5 metres
▶ Install EMI filter at input for sensitive electronic environments
▶ Never use a contactor on the output side without VFD interlock
▶ Set motor overload P06.01 = motor FLA for proper protection
▶ For PLC integration: use sink/source jumper matching PLC output type
▶ RS-485 Modbus: use 120Ω termination resistor at last device
▶ Always verify drive rating ≥ motor kW before installation

## Slide 23
Course Summary
✔ Module 01: VFD basics, working principle, advantages
✔ Module 02: Delta VFD-M model codes, specs, accessories
✔ Module 03: Safety — DANGER / WARNING / CAUTION guidelines
✔ Module 04: Mechanical installation, clearances, environment
✔ Module 05: Power & control terminal wiring (R/S/T, U/V/W, MI, AVI, ACI)
✔ Module 06: Keypad operation, LED display, navigation
✔ Module 07: Parameter groups P00–P09 — complete programming
✔ Module 08: Speed reference sources & run/stop control modes
✔ Module 09: Auto-tuning, V/F curve, DC braking, optimization
✔ Module 10: Fault codes (OC/OV/UV/OL/OH) & protection settings
✔ Module 11: Applications — pump PID, CNC spindle, multi-speed
✔ Module 12: Maintenance schedule & troubleshooting guide
Thank You for Completing the Delta VFD-M Training Course!
Delta Electronics | Industrial Automation Training Division
For technical support: www.delta-ia.com.tw | support@deltaww.com
© Delta Electronics — All Rights Reserved